## Transmission Cost Calculator
Black & Veatch Transmission Line Capital Cost Calculator | [5 empty] | User Selection
Auto-calculated
| Selection | Multiplier | Cumulative Cost/Mile | Column # |  | Adjustable Parameter
Voltage Class | 345 kV Single Circuit | 1 | 1434290 | 3
Conductor Type | ACSR | 1 | 1434290
Structure | Lattice | 1 | 1434290
Length Category | > 10 miles | 1 | 1434290
New or Re-conductor? | New | 1 | 1434290
Average Terrain Multiplier | 1 | 1.405 | 2015177.45
Terrain Type | Miles of Terrain Type | Multiplier | Weighted Miles
Forested | 0.125 | 2.25 | 0.28125
Scrubbed/Flat | 0.125 | 1 | 0.125
Wetland | 0.125 | 1.2 | 0.15
Farmland | 0.125 | 1 | 0.125
Desert/Barren Land | 0.125 | 1.05 | 0.13125
Urban | 0.125 | 1.59 | 0.19875
Rolling Hills (2-8% Slope) | 0.125 | 1.4 | 0.175
Mountain (>8% Slope) | 0.125 | 1.75 | 0.21875
Total Miles | 1
BLM Cost Zone Number | ROW Miles in BLM Zone | $/Acre | $/Mile of ROW | Zone ROW Costs
1 | 0.1 | 83.061 | 1761.9 | 176.19
2 | 0.1 | 160.776 | 3410.4 | 341.04
3 | 0.1 | 314.325 | 6667.5 | 666.75
4 | 0.1 | 473.715 | 10048.5 | 1004.85
5 | 0.1 | 652.509 | 13841.1 | 1384.11
6 | 0.1 | 942.381 | 19989.9 | 1998.99
7 | 0.1 | 1317.69 | 27951 | 2795.1
8 | 0.1 | 837.738 | 17770.2 | 1777.02
9 | 0.1 | 4519.845 | 95875.5 | 9587.55
10 | 0.1 | 13882.374 | 294474.6 | 29447.46
11 | 0 | 27764.748 | 588949.2 | 0
12 | 0 | 69411.771 | 1472370.9 | 0
13 | 0 | 138823.542 | 2944741.8 | 0
14 | 0 | 208235.313 | 4417112.7 | 0
15 | 0 | 277647.084 | 5889483.6 | 0
AFUDC/Overhead Cost | 17.5%
Project Cost Results | Per Mile | Total
Line Cost | 2015177.45 | 2015177.45 |  |  | Per Mile (MW/Mile) | Total (MW)
ROW Cost | 49179.06 | 49179.06 |  | Project Line Losses | 0.16061 | 0.16061
AFUDC/Overhead Cost | 361262.3893 | 361262.3893
All Costs | 2425618.8992 | 2425618.8992
Transmission Cost Assumptions, ROW Widths, and Land Costs
Equipment | 230 kV Single Circuit | 230 kV Double Circuit | 345 kV Single Circuit | 345 kV Double Circuit | 500 kV Single Circuit | 500 kV Double Circuit | 500 kV HVDC Circuit | 600 kV HVDC Circuit
Column # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Initial Cost | 1024335 | 1639820 | 1434290 | 2295085 | 2048670 | 3278535 | 1639820 | 1721811
Multipliers
Conductor
ACSR | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ACSS | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
HTLS | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
Structure
Lattice | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1
Tubular Steel | 1 | 1 | 1.30 | 1.3 | 1.5 | 1.5 | 1.5 | 1.5
Length
> 10 miles | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3-10 miles | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
< 3 miles | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Age
New | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Re-conductor | 0.35 | 0.45 | 0.45 | 0.55 | 0.55 | 0.65 | 0.55 | 0.55
Right-of-Way Widths | 230 kV Single Circuit | 230 kV Double Circuit | 345 kV Single Circuit | 345 kV Double Circuit | 500 kV Single Circuit | 500 kV Double Circuit | 500 kV HVDC Circuit | 600 kV HVDC Circuit
Width (ft.) | 125 | 150 | 175 | 200 | 200 | 250 | 200 | 225
Acres/mile | 15.1515 | 18.1818 | 21.2121 | 24.2424 | 24.2424 | 30.303 | 24.2424 | 27.2727
| BLM Zone Land Costs |  |  | Converting Per Acre Rent to Land Market Value
BLM Zone Number | 2018 Per Acre Rent ($/acre-year) | Land Market Value ($/acre) |  | Land Tax Rate | 1% | of rent
1 | 8.39 | 83.061 |  | Capitalization Rate | 10%
2 | 16.24 | 160.776
3 | 31.75 | 314.325
4 | 47.85 | 473.715 |  | Updating Base Cost Values from 2012 to 2018 Dollars
5 | 65.91 | 652.509 |  | Inflation Rate (2012-2018) |  | 10.5%
6 | 95.19 | 942.381
7 | 133.1 | 1317.69
8 | 84.62 | 837.738
9 | 456.55 | 4519.845
10 | 1402.26 | 13882.374
11 | 2804.52 | 27764.748
12 | 7011.29 | 69411.771
13 | 14022.58 | 138823.542
14 | 21033.87 | 208235.313
15 | 28045.16 | 277647.084
Assumed Line Utilization | 60%
Full Load Adjustment | 0.48
| 230 kV Single Circuit | 230 kV Double Circuit | 345 kV Single Circuit | 345 kV Double Circuit | 500 kV Single Circuit | 500 kV Double Circuit | 500 kV HVDC Circuit | 600 kV HVDC Circuit
Capacity | 400 | 800 | 750 | 1500 | 1500 | 3000 | 3000 | 3000
Phase Current (amps) | 1056.9341 | 1056.9341 | 1321.1677 | 1321.1677 | 1823.2114 | 1823.2114 | 3000 | 2500
No. Conductors Per Phase | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 3
No. Circuits Per Line | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 2
No. Phases | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 1
ACSR Size | 1272 | 1272 | 795 | 795 | 1590 | 1590 | 1780 | 1780
Resistance | 0.08305 | 0.08305 | 0.1278 | 0.1278 | 0.06765 | 0.06765 | 0.057344 | 0.057344
ACSS Size | 477 | 477 | 336.4 | 336.4 | 605 | 605 | 636 | 636
Resistance | 0.2253 | 0.2253 | 0.319 | 0.319 | 0.178 | 0.178 | 0.15378 | 0.15378
HTLS | 477 | 477 | 336 | 336 | 557 | 557 | 636 | 636
Resistance | 0.2275 | 0.2275 | 0.315 | 0.315 | 0.186 | 0.186 | 0.1635 | 0.1493
Line Loss MW / Mile | 230 kV Single Circuit | 230 kV Double Circuit | 345 kV Single Circuit | 345 kV Double Circuit | 500 kV Single Circuit | 500 kV Double Circuit | 500 kV HVDC Circuit | 600 kV HVDC Circuit
ACSR | 0.1336 | 0.26719 | 0.16061 | 0.32122 | 0.10794 | 0.21588 | 0.16515 | 0.11469
ACSS | 0.36243 | 0.72485 | 0.4009 | 0.80181 | 0.28401 | 0.56802 | 0.44287 | 0.30755
HTLS | 0.36597 | 0.73193 | 0.39588 | 0.79175 | 0.29678 | 0.59355 | 0.47088 | 0.29859
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10

## Substation Cost Calculator
Black & Veatch Substation Capital Cost Calculator |  |  |  |  | User Selection
Auto-calculated
| Selection |  | Cost Component | Cost | Adjustable Parameter
Voltage | 345 kV Substation |  | Base Cost | N/A
New or Existing Site? | Existing |  | Circuit Breakers | 10755517.5
Circuit Breaker Type | Breaker and a Half |  | HVDC Converter | 0
# of Line/XFMR Positions | 3 |  | Transformer(s) | 13260000
HVDC Converter | No |  | SVC(s) | 0
Transformer Type | 230/345 kV XFMR |  | Shunt Reactor(s) | 0
MVA Rating Per Transformer | 1200 |  | Series Capacitor(s) | 0
# of Transformers | 1 |  | AFUDC/Overhead Cost | 4202715.5625
SVC MVAR Rating | 0
Shunt Reactor MVAR Rating | 0 |  | Total Substation Cost | 28218233.0625
Series Capacitor MVAR Rating | 0
AFUDC/Overhead Cost | 17.5%
Column # | 2
Substation Cost Assumptions
Equipment | 230 kV Substation | 345 kV Substation | 500 kV Substation
Column # | 1 | 2 | 3
Base Cost (New Substation) | 1821040 | 2276300 | 2731560
Cost Per Line Position | 1593410 | 2390115 | 3186820
Ring Bus | 1 | 1 | 1
Breaker and a Half | 1.5 | 1.5 | 1.5
500 kV HVDC Converter |  |  | 491725000
600 kV HVDC Converter |  |  | 540897500
Shunt Reactor Cost ($/MVAR) | 22100 | 22100 | 22100
Series Capacitor Cost ($/MVAR) | 33150 | 11050 | 11050
SVC Cost ($/MVAR) | 93925 | 93925 | 93925
Transformer Cost ($/MVA)
115/230 kV XFMR | 7735
115/345 kV XFMR |  | 11050
115/500 kV XFMR |  |  | 11050
138/230 kV XFMR | 7735
138/345 kV XFMR |  | 11050
138/500 kV XFMR |  |  | 11050
230/345 kV XFMR |  | 11050
230/500 kV XFMR | 12155 |  | 12155
345/500 kV XFMR |  | 14365 | 14365
Updating Base Cost Values from 2012 to 2018 Dollars
Inflation Rate (2012-2018) | 10.5%
Existing
500 kV HVDC Converter
600 kV HVDC Converter
No

## Cost Totals
Black & Veatch Transmission and Substation Cost Totals
| Project Cost Results | Per Mile | Total | User Selection
| Line Cost | 2015177.45 | 2015177.45 | Auto-calculated
| ROW Cost | 49179.06 | 49179.06
| Substation #1 | N/A | 28218233.0625
| Substation #2 | N/A | 0
| Substation #3 | N/A
| Substation #4 | N/A
| Substation #5 | N/A
| AFUDC/Overhead Cost | 361262.3893 | 5299453.1752
| All Costs | 2425618.8992 | 35582042.7477
Total (MW)
| Average Losses | 0.16061